| ID:54 |  | - specialised surfaces (partucularly metals) in industrial buildings |
| --- | --- | --- |
| Cleaning of contaminated (industrial) ventilation systems |  |  |
| Objective | To reduce external doses arising from contamination in ventilation systems in industrial buildings. |  |
| Other benefits | Will remove contamination from the area and prevent redistribution of contamination in buildings. |  |
| Countermeasure description | The Chernobyl accident showed that industrial ventilation systems may become heavily contaminated and are not very easy to decontaminate. Cleaning involves industrial vacuum cleaning, washing with chemical solutions and possibly use of an electrical rotating brush in narrow ventilation ducts. In channels with larger diameters (ca. 50 cm) it is often necessary for a person to enter the duct with a 'NORCLEAN' type industrial vacuum cleaner. Alternatively, it may be possible to open the ventilation system and hose it at high pressure with water. |  |
| Target surface or population | Highly contaminated (industrial) ventilation systems. |  |
| Target radionuclides | All radionuclides. Should not be considered for removal of short-lived radionuclides alone. |  |
| Scale of application | Could be carried out on a medium scale in highly contaminated industrial areas. |  |
| Timing of implementation | Maximum benefit if carried out shortly after deposition. Can have a significant effect on reducing contamination levels even if applied a decade after contamination. |  |
| Constraints on implementation |  |  |
| Legal | Liabilities for possible damage to property. Possible regulations on chemical use. |  |
| Environmental / technical |  |  |
| Effectiveness |  |  |
| Reduction in contamination on the surface | Expected % reduction in contamination levels is 80-97% by high pressure hosing or in the region of 80-90% by vacuuming/brushing |  |
| Reduction in surface dose rates | Not estimated. |  |
| Reduction in resuspension | Not estimated. |  |
| Averted doses | Doses received by members of the public working in these buildings will depend on a number of factors, in particular the amount of time spent in the vicinity of ventilation ducts. No estimates of averted doses have been made. Riso – is there anything else we can say here re effectiveness based on Chernobyl experience? |  |
| Additional doses | Exposure pathways workers could be exposed to are: - External exposure from environment and contaminated equipment - Enhanced resupension leading to inhalation of dust - Inadvertent ingestion of dust from workers' hands Contributions from pathways in italics are unlikely to be significant and doses from these pathways can be controlled by using PPE. Exposure routes from transport and disposal of waste are not included. The dose over a day to a worker implementing decontamination of ventilation ducts may be significantly higher than that to an individual living or working in the contaminated area as very high contamination levels can build up in ventilation systems, especially in filters. This depends on the size of filter and filter system (i.e. requirement to climb into system or possibility for external handling). Dose rates must be assessed prior to any time-consuming action). No illustrative doses have been estimated as they will be very specific to the type of contamination, the tasks undertaken by an individual, controls placed on working and the use of PPE. |  |
| Factors influencing effectiveness of procedure (technical) | The physical-chemical form of the contaminant aerosol type (size, solubility). Operator skills. Pressure and amount of water for high pressure water treatment. Water temperature because the air outlet channels, in particular may be greasy and contain dust; a high water temperature is therefore needed to get a high reduction in contamination levels. However, it should be noted that the inlet channels are usually the most contaminated. |  |
| Factors influencing effectiveness of procedure (social) |  |  |
| Requirements |  |  |
| Required specific equipment | Brushes, vacuum device, 'dust trap' filter and/or 'NORCLEAN' type industrial vacuum cleaner and/or high pressure water washer and possibly grinding machines and other hand tools. |  |
| Required utilities and infrastructure | Transport vehicles for equipment. Scaffolding or mobile lifts for tall buildings, where channels may be mounted under the ceiling. |  |
| Required consumables | Water supply. Pressurised air supply. |  |
| Required skills | Skilled personnel required. Industrial cleaning companies will have the required skills. |  |
| Required safety precautions | In tall buildings, where ventilation systems are mounted high up, lifelines are required. Safety helmets. Water proof safety clothing. Respiratory protection is recommended. |  |
| Waste |  |  |
| Amount and type | Generates some 50 – 100 g per m2 of solid waste. (Solid waste contamination level: ca. 10 – 20 kBq m-3 per Bq m-2). Dry waste is collected in vacuuming filters that are relatively easy to dispose of. Wet waste from pressure washing can mostly be collected and filtered with the industrial vacuum cleaner, so that the water is cleaned and sludge is left. |  |
| Intervention costs |  |  |
| Equipment | Brushes, vacuum device, 'dust trap' filter: total ca. 6,000 EURO. 'NORCLEAN' type industrial vacuum cleaner with accessories: ca. 7,000 EURO. High pressure water washer: typically ca. 3000 EURO. Grinding machines and other hand tools: probably ca. 1,000 EURO. Variable costs for scaffolding/lifts according to need. |  |
| Consumables | Ca. 25 l per min. of water for pressure washing. Power (380 v) and pressurised air and petrol for equipment transport; at current prices. Alkaline detergent for pressure washing: ca. 100 EURO per 100 l detergent (sufficient for 2500 l water). |  |
| Operator time | Small ventilation channels (<20 cm in diameter): typically ca. 50 m per 8 hour working day In larger channels typically 2 – 3 m2 per h. If there are valves, these must be dismounted. Each valve takes ca. 1.5 h. Treatment of large ventilator drums and ventilator house often requires significant additional time (several hours - motors and electrical installations must be dismounted first). Variable time for setting up scaffolds/transport. |  |
| Factors influencing costs | The following factors influence the time taken to implement the option and hence labour costs: - Need for scaffolds /mobile lifts. - Need for different types of treatment (dependant on e.g., channel sizes and other ventilation system characteristics). Cost of specialist labour |  |
| Side effects / impact |  |  |
| Environmental impact | The disposal or storage of waste arising from the implementation of this option may have an environmental impact. However, this should be minimised through the control of any disposal route and relevant authorisations. Electronic parts may be damaged by water if not dismounted, Loss of lifetime of equipment due to the mechanical impact (e.g. the basic material will be thinner and rough). |  |
| Social impact | - Acceptability of disposal of contaminated waste. Removal of the corrosion products from the surface; the ventilation system is cleaned, and is expected to run better Reassurance of employees and users and maintaining continuity of work. |  |
| Practical experience | Tested in a number of industrial buildings in the CIS and Europe, after the Chernobyl accident. |  |
| Key references | Eged et al (2003); Hubert et al (1996); Johnsson (1997) |  |